## Equipment
Tag | Description | System | Manufacturer | Model | Qty | Owner / furnished by | BOM ref | Weight (kg) | X (ft) | Y (ft) | Base Z (ft) | Foundation | Location | Library status | Source
BES-CNT01 | GOTION#1 (B-type) | BES | Gotion | ESD1331-05P5015 | 1 | FortifyGrid | 202 | 43000 | 86.42 | 23 | 0.5 | STR-FDN-B1 | drawing | baseline | Gotion BESS ESD1331-05P5015.pdf (datasheet v2.0, p.14)
BES-CNT02 | GOTION#2 (A-type) | BES | Gotion | ESD1331-05P5015 | 1 | FortifyGrid | 202 | 43000 | 69.08 | 23 | 0.5 | STR-FDN-B2 | drawing | baseline | Gotion BESS ESD1331-05P5015.pdf (datasheet v2.0, p.14)
BES-CNT03 | GOTION#3 (B-type) | BES | Gotion | ESD1331-05P5015 | 1 | FortifyGrid | 202 | 43000 | 34.42 | 23 | 0.5 | STR-FDN-B3 | drawing | baseline | Gotion BESS ESD1331-05P5015.pdf (datasheet v2.0, p.14)
BES-CNT04 | GOTION#4 (A-type) | BES | Gotion | ESD1331-05P5015 | 1 | FortifyGrid | 202 | 43000 | 17.08 | 23 | 0.5 | STR-FDN-B4 | drawing | baseline | Gotion BESS ESD1331-05P5015.pdf (datasheet v2.0, p.14)
PCS-SKD01 | PCS/MVT skid 1 (serves GOTION#3, #4) | PCS | Sineng | EH-4200-HB-UD-US-12.47 | 1 | FortifyGrid | B01 | 20000 | 34.33 | 53.4 | 0.5 | STR-FDN-P1 | drawing | baseline | Sineng 5MW datasheet 12.47kV; E101 BESS equipment layout (07-08-2026)
PCS-SKD02 | PCS/MVT skid 2 (serves GOTION#1, #2) | PCS | Sineng | EH-4200-HB-UD-US-12.47 | 1 | FortifyGrid | B01 | 20000 | 69 | 53.4 | 0.5 | STR-FDN-P2 | drawing | baseline | Sineng 5MW datasheet 12.47kV; E101 BESS equipment layout (07-08-2026)
AUX-RCK01 | Unistrut equipment rack (MB, DP, MPC, UPS, EMS, telecom) | AUX | Electrical contractor | Unistrut frame | 1 | Electrical contractor | J01 | 300 | 112.08 | 14.5 | 0.5 | STR-FDN-R1 | drawing | baseline | Comstock 60% BOM J01; E101 overall site plan (18'-2")
AUX-MB01 | Main circuit breaker 480 V 400 A 65 kA, NEMA 3R | AUX | AD Stanley supply | 400 A MCB | 1 | AD Stanley | C01 | 80 | 104.5 | 14.5 | 1 |  | drawing | baseline | Comstock 60% BOM C01
AUX-DP01 | Distribution panel 480/277 V 400 A 65 kA, NEMA 3R | AUX | AD Stanley supply | 400 A panelboard | 1 | AD Stanley | C02 | 120 | 106.8 | 14.5 | 1 |  | drawing | baseline | Comstock 60% BOM C02
AUX-MPC01 | Mini power center 15 kVA 480-120/240 V, NEMA 3R | AUX | AD Stanley supply | MPC 15 kVA | 1 | AD Stanley | C03 | 180 | 109 | 14.5 | 1 |  | drawing | baseline | Comstock 60% BOM C03
AUX-UPS01 | MicroCab 1500 outdoor DC UPS 24 VDC, NEMA 3RX | AUX | AD Stanley supply | MicroCab 1500 | 1 | AD Stanley | C04 | 90 | 111.2 | 14.5 | 1 |  | drawing | baseline | Comstock 60% BOM C04
EMS-PNL01 | EMS / PPC panel (Terabase controller, gateways, switches, firewall, GPS clock) | EMS | AD Stanley enclosure; Terabase internals | NEMA 3R EMS panel | 1 | AD Stanley (enclosure) / Terabase (internals) | C05 | 150 | 113.6 | 14.5 | 1 |  | drawing | baseline | Comstock 60% BOM C05; Terabase EMS Contract v7 Annexure A
EMS-TEL01 | Telecom panel (WAN primary + secondary) | EMS | AD Stanley enclosure | NEMA 3R telecom panel | 1 | AD Stanley (panel) / Owner (WAN service) | C06 | 60 | 116.5 | 14.5 | 1 |  | drawing | baseline | Comstock 60% BOM C06
UI-AEP-P1 | AEP pole 1 — auxiliary tap | UI | Various | 45 ft Class 2 SYP | 1 | AEP |  | 900 | 132 | 112 | 0 |  | approximate | baseline | Comstock 60% BOM pole item 1
UI-AEP-P2 | AEP pole 2 — telecom 10 kVA service | UI | Various | 45 ft Class 2 SYP | 1 | AEP |  | 900 | 110 | 112 | 0 |  | approximate | baseline | Comstock 60% BOM pole item 1
UI-AEP-P3 | AEP pole 3 — 800 A Viper recloser | UI | Various | 45 ft Class 2 SYP | 1 | AEP |  | 900 | 88 | 112 | 0 |  | approximate | baseline | Comstock 60% BOM pole item 1
UI-AEP-P4 | AEP pole 4 — primary meter | UI | Various | 45 ft Class 2 SYP | 1 | AEP |  | 900 | 66 | 112 | 0 |  | approximate | baseline | Comstock 60% BOM pole item 1
UI-AEP-P5 | AEP pole 5 — 900 A GOAB switch (ownership boundary) | UI | Various | 45 ft Class 2 SYP | 1 | AEP |  | 900 | 44 | 112 | 0 |  | approximate | baseline | Comstock 60% BOM pole item 1
UI-AXT01 | AEP 3-phase pad-mount aux transformer 277/480 V | UI | AEP furnished | 3-ph pad-mount 75-750 kVA 277/480 V | 1 | AEP |  | 2000 | 118 | 28 | 0 |  | approximate | baseline | AEP Three Phase Padmount Xfmr Specs 4-10-26
UI-POL01 | Customer recloser pole | UI | Various | 45 ft Class 2 SYP | 1 | Electrical contractor |  | 900 | 34 | 106 | 0 |  | approximate | baseline | Comstock 60% BOM pole item 1
UI-POL02 | Service riser pole (P6) | UI | Various | 45 ft Class 2 SYP | 1 | Electrical contractor |  | 900 | 24 | 102 | 0 |  | approximate | baseline | Comstock 60% BOM pole item 1
SSV-LTG01 | Light pole with 2 x 400 W LED floodlights | SSV | Electrical contractor | LED flood 400 W | 1 | Electrical contractor | K01 | 200 | 100 | 30 | 0 |  | approximate | baseline | Comstock 60% BOM J02, K01
UI-AEP-RCL | AEP utility recloser 800 A (Viper) | UI | G&W (AEP furnished) | Viper 800 A | 1 | AEP |  | 400 | 88 | 109.49 | 26 |  | drawing | baseline | AEP 5 Pole Layout (D.S. 1825-D)
UI-AEP-MTR | AEP primary revenue metering (CT/PT + meter) | UI | AEP | Primary metering | 1 | AEP |  | 300 | 66 | 109 | 24 |  | drawing | baseline | AEP 5 Pole Layout; AEP Metering details.docx
UI-DS01 | Visible open point (POI) | UI | S&C Electric | 18932-C / 137192R2-E-Z5-T200 | 1 | AEP | A01 | 250 | 44 | 107.52 | 36 |  | drawing | baseline | Comstock 60% BOM A01; AEP 5 Pole Layout
MV-RCL01 | G&W 3-phase recloser, 15 kV | MV | G&W Electric | 15 kV 3-ph recloser | 1 | FortifyGrid | A03 | 400 | 34 | 103.49 | 26 |  | drawing | baseline | Comstock 60% BOM A03
MV-REL01 | SEL-651R2 recloser control | MV | Schweitzer Engineering Laboratories | SEL-651R2 | 1 | FortifyGrid | A04 | 60 | 34 | 104.31 | 5 |  | drawing | baseline | Comstock 60% BOM A04; AEP interconnection requirements
UI-SA01 | Distribution-class surge arrester 10 kV, 8.4 kV MCOV | UI | Eaton | URT1005-0A1A-1B1A | 3 | AD Stanley | A02 | 9 | 24 | 101.26 | 34 |  | drawing | baseline | Comstock 60% BOM A02

## Cable Schedule
Cable | From | To | Purpose | Voltage | Route | Conduit qty | Conduit size (in) | Conductors | Route length (ft) | Cable length per conductor (ft) | Trench segments | Status | Note
OH01 | UI-AEP-P1 | UI-AEP-P5 | AEP distribution feeder | 12.47 kV | OH |  |  | by others | 88 | 89.8 |  | schedule
OH02 | UI-AEP-P5 | UI-POL02 | Customer overhead tap to recloser and riser poles | 12.47 kV | OH |  |  | by others | 22.4 | 22.9 |  | schedule | 477 AAC 'Cosmos' per pole BOM
P01 | UI-POL02:riser | PCS-SKD01:mv | BESS feeder | 12.47 kV | UG | 1 | 5 | 3 x 1/C 750 kcmil Cu, 15 kV, 100% EPR, MV-105; 1 x 1/C #2/0 AWG Cu ground / neutral | 55.3 | 71.3 | M0-M1, M1-M2, M2-S1 | revised | E-403: Pole P6 -> TR-1. Now terminates on Sineng skid 1
P02 | PCS-SKD01:mv | PCS-SKD02:mv | MV loop skid 1 to skid 2 | 12.47 kV | UG | 1 | 5 | 3 x 1/C 750 kcmil Cu, 15 kV, 100% EPR, MV-105; 1 x 1/C #2/0 AWG Cu ground / neutral | 50.7 | 66.7 | S1-S2 | revised
P03 | BES-CNT01:dc | PCS-SKD02:dc | DC power | 1500 VDC | UG | 4 | 4 | 16 x 1/C 500 kcmil DLO tinned Cu, 2000 V, RHH/RHW-2 | 36.4 | 52.4 | D1-D2 | revised | Re-verify conductor count for Sineng DC inputs
P04 | BES-CNT02:dc | PCS-SKD02:dc | DC power | 1500 VDC | UG | 4 | 4 | 16 x 1/C 500 kcmil DLO tinned Cu, 2000 V, RHH/RHW-2 | 19 | 35 |  | revised
P05 | BES-CNT03:dc | PCS-SKD01:dc | DC power | 1500 VDC | UG | 4 | 4 | 16 x 1/C 500 kcmil DLO tinned Cu, 2000 V, RHH/RHW-2 | 19 | 35 |  | revised
P06 | BES-CNT04:dc | PCS-SKD01:dc | DC power | 1500 VDC | UG | 4 | 4 | 16 x 1/C 500 kcmil DLO tinned Cu, 2000 V, RHH/RHW-2 | 36.3 | 52.3 | D4-DW, D3-DW | revised
P08 | UI-AEP-P1:base | UI-AXT01:hv | Aux transformer feeder | 12.47 kV | UG | 1 | 4 | by others | 106.4 | 122.4 | A1-A2, A2-A3 | schedule | Conductors by AEP
P09 | UI-AXT01:lv | AUX-MB01:p | Aux service | 480 VAC | UG | 2 | 3 | 6 x 1/C 250 kcmil Cu XHHW-2, 600 V; 2 x 1/C #2 AWG Cu ground XHHW-2 | 41.7 | 57.7 | A3-R1, R0-R1 | schedule
P10 | AUX-MB01 | AUX-DP01 | Main breaker to panel | 480 VAC | AG | 2 | 3 | 6 x 1/C 250 kcmil Cu XHHW-2, 600 V; 2 x 1/C #2 AWG Cu ground XHHW-2 | 2.3 | 18.3 |  | schedule
P11 | AUX-DP01 | AUX-MPC01 | Panel to mini power center | 480 VAC | AG | 1 | 0.75 | 3 x 1/C #10 AWG Cu XHHW-2, 600 V; 1 x 1/C #10 AWG Cu ground XHHW-2 | 2.2 | 18.2 |  | schedule
P12 | AUX-DP01:p | BES-CNT01:aux | Container aux AUX 1.1 | 480 VAC | UG | 1 | 1.5 | 3 x 1/C #4 AWG Cu XHHW-2, 600 V; 1 x 1/C #8 AWG Cu ground XHHW-2 | 65.3 | 81.3 | R0-R1, DE-R1, D1-DE | schedule
P13 | AUX-DP01:p | BES-CNT02:aux | Container aux AUX 2.1 | 480 VAC | UG | 1 | 1.5 | 3 x 1/C #4 AWG Cu XHHW-2, 600 V; 1 x 1/C #8 AWG Cu ground XHHW-2 | 82.7 | 98.7 | R0-R1, DE-R1, D1-DE, D1-D2 | schedule
P14 | AUX-DP01:p | BES-CNT03:aux | Container aux AUX 3.1 | 480 VAC | UG | 1 | 1.5 | 3 x 1/C #4 AWG Cu XHHW-2, 600 V; 1 x 1/C #8 AWG Cu ground XHHW-2 | 117.3 | 133.3 | R0-R1, DE-R1, D1-DE, D1-D2, D2-DM, D3-DM | schedule
P15 | AUX-DP01:p | BES-CNT04:aux | Container aux AUX 4.1 | 480 VAC | UG | 1 | 1.5 | 3 x 1/C #4 AWG Cu XHHW-2, 600 V; 1 x 1/C #8 AWG Cu ground XHHW-2 | 134.7 | 150.7 | R0-R1, DE-R1, D1-DE, D1-D2, D2-DM, D3-DM, D3-DW, D4-DW | schedule
C01 | EMS-PNL01:com | BES-CNT01:com | BMS Modbus-TCP | comms | UG | 1 | 1 | 1 x Cat 5e shielded | 62.1 | 78.1 | R0-R1, DE-R1, D1-DE | proposed
C02 | EMS-PNL01:com | BES-CNT02:com | BMS Modbus-TCP | comms | UG | 1 | 1 | 1 x Cat 5e shielded | 79.5 | 95.5 | R0-R1, DE-R1, D1-DE, D1-D2 | proposed
C03 | EMS-PNL01:com | BES-CNT03:com | BMS Modbus-TCP | comms | UG | 1 | 1 | 1 x Cat 5e shielded | 114.1 | 130.1 | R0-R1, DE-R1, D1-DE, D1-D2, D2-DM, D3-DM | proposed
C04 | EMS-PNL01:com | BES-CNT04:com | BMS Modbus-TCP | comms | UG | 1 | 1 | 1 x Cat 5e shielded | 131.5 | 147.5 | R0-R1, DE-R1, D1-DE, D1-D2, D2-DM, D3-DM, D3-DW, D4-DW | proposed
C05 | EMS-PNL01:com | PCS-SKD01:com | PCS Modbus-TCP / IEC 61850 | comms | UG | 1 | 1 | 1 x 6-strand 50 um OM2 multimode fiber | 115.4 | 131.4 | R0-R1, DE-R1, D1-DE, D1-D2, D2-DM, D3-DM | proposed
C06 | EMS-PNL01:com | PCS-SKD02:com | PCS Modbus-TCP / IEC 61850 | comms | UG | 1 | 1 | 1 x 6-strand 50 um OM2 multimode fiber | 80.8 | 96.8 | R0-R1, DE-R1, D1-DE, D1-D2 | proposed
C07 | EMS-PNL01:com | MV-REL01:com | Recloser control DNP3 (AEP telemetry path) | comms | UG | 1 | 1 | 1 x 6-strand 50 um OM2 multimode fiber | 195.9 | 211.9 | R0-R1, DE-R1, D1-DE, D1-D2, D2-DM, D3-DM, D3-DW, DW-M2, M1-M2, M0-M1 | proposed
C08 | EMS-PNL01 | EMS-TEL01 | WAN uplink | comms | AG | 1 | 0.75 | 1 x Cat 5e shielded | 2.9 | 18.9 |  | proposed

## Trench Schedule
Segment | Length (ft) | Cables | Systems | Conduits | Largest conduit (in) | Single-layer width (in, prelim.)
A2-A1 | 84 | P08 | UI | 1 | 4 | 10
A3-A2 | 8 | P08 | UI | 1 | 4 | 10
D1-DE | 25.6 | P12, P13, P14, P15, C01, C02, C03, C04, C05, C06, C07 | AUX, EMS | 11 | 1.5 | 49
D2-D1 | 17.4 | P03, P13, P14, P15, C02, C03, C04, C05, C06, C07 | AUX, BES, EMS | 13 | 4 | 68.5
D3-DM | 17.3 | P14, P15, C03, C04, C05, C07 | AUX, EMS | 6 | 1.5 | 28
D4-DW | 6.9 | P06, P15, C04 | AUX, BES, EMS | 6 | 4 | 39.5
DE-R1 | 14.2 | P12, P13, P14, P15, C01, C02, C03, C04, C05, C06, C07 | AUX, EMS | 11 | 1.5 | 49
DM-D2 | 17.3 | P14, P15, C03, C04, C05, C07 | AUX, EMS | 6 | 1.5 | 28
DW-D3 | 10.4 | P06, P15, C04, C07 | AUX, BES, EMS | 7 | 4 | 43.5
DW-M2 | 28.8 | C07 | EMS | 1 | 1 | 7
M1-M0 | 8 | P01, C07 | EMS, MV | 2 | 5 | 15
M2-M1 | 24 | P01, C07 | EMS, MV | 2 | 5 | 15
M2-S1 | 10.3 | P01 | MV | 1 | 5 | 11
R1-A3 | 12 | P09 | AUX | 2 | 3 | 15
R1-R0 | 7 | P09, P12, P13, P14, P15, C01, C02, C03, C04, C05, C06, C07 | AUX, EMS | 13 | 3 | 61
S1-S2 | 34.7 | P02 | MV | 1 | 5 | 11

## Foundation Loads
Foundation | Status | Supports | Area (ft²) | Equipment (kip) | Slab (kip) | Pressure (psf) | Utilisation vs 2000 psf
STR-FDN-B1 | existing | BES-CNT01 | 218.3 | 94.8 | 49.1 | 659 | 0.33
STR-FDN-B2 | existing | BES-CNT02 | 218.3 | 94.8 | 49.1 | 659 | 0.33
STR-FDN-B3 | existing | BES-CNT03 | 218.3 | 94.8 | 49.1 | 659 | 0.33
STR-FDN-B4 | existing | BES-CNT04 | 218.3 | 94.8 | 49.1 | 659 | 0.33
STR-FDN-BX | existing_unused |  | 218.3 | 0 | 49.1 | 225 | 0.113
STR-FDN-P1 | new | PCS-SKD01 | 227.5 | 44.1 | 51.2 | 419 | 0.209
STR-FDN-P2 | new | PCS-SKD02 | 227.5 | 44.1 | 51.2 | 419 | 0.209
STR-FDN-PX1 | existing_unused |  | 133 | 0 | 29.9 | 225 | 0.113
STR-FDN-PX2 | existing_unused |  | 133 | 0 | 29.9 | 225 | 0.113
STR-FDN-R1 | new | AUX-RCK01 | 36.3 | 0.7 | 5.5 | 168 | 0.084

## MTO vs 60% BOM
BOM ref | Model description | Unit | Model qty | 60% BOM qty | Delta | 60% BOM description
202 | Gotion GRID 5015 liquid-cooled BESS container | EA | 4 | 4 | 0 | MAKE : GOTION, MODEL:ESD1331-05P5015 5.015MWh. PRODUCT MODEL : ESD1331-05P5015 APPROX. DIMENSION & WEIGHT : 238.5in×9 6
A01 | Gang-operated air-break switch 15.5 kV 900 A (S&C solid blade) | EA | 1 |  |  | SOLID BLADE DISCONNECTS, 15.5 KV MAX., 110 KV BIL, 900 AMPS, 36 KA MOMENTARY, WITH TIN-PLATED BRONZE CONNECTOR FOR #2 AW
A02 | Distribution-class surge arrester 10 kV, 8.4 kV MCOV | EA | 3 | 3 | 0 | SURGE ARRESTERS, DISTRIBUTION CLASS, 10 KV, 8.40 KV MCOV
A03 | G&W 3-phase recloser, 15 kV | EA | 1 | 1 | 0 | 3 PHASE RECLOSER, 15 KV, 110 KV BIL, 630 AMP, 12.5 KA SYM. SHORT CIRCUIT RATING; 3-STAGE AUXILIARY SWITCH; 30 FT AUXILIA
A04 | SEL-651R2 recloser control | EA | 1 |  |  | RECLOSER CONTROL, SCHWEITZER SEL-651R2, WITH: 3-EIA-232, USB, COMMUNICATIONS PORT; 2-10/100 BASE-T, 1-EIA-485 COMMUNICAT
B01 | Sineng PCS + MV turnkey station (4 x 1250 kW PCS, 4.2 MVA transformer) | EA | 2 | 4 | -2 | Dynapower CPS-2500 Gen5 bidirectional PCS rated 2304 kW, 690 VAC, 60 Hz, DC input range 981–1500 VDC, UL 1741 SB, IEEE 1
C01 | Main circuit breaker 480 V 400 A 65 kA, NEMA 3R | EA | 1 | 1 | 0 | MAIN CIRCUIT BREAKER,480V AC, 400A (3P), 3PH, 60HZ, 4W, 65kA, NEMA 3R OUTDOOR ENCLOSURE, UNISTRUT MOUNTED.
C02 | Distribution panel 480/277 V 400 A 65 kA, NEMA 3R | EA | 1 | 1 | 0 | OUTDOOR MAIN AC DISTRIBUTION PANEL, NEMA 3R, 480V/277V AC, 3-PHASE, 4-WIRE, 400 AMP, 65KA, SOLID NEUTRAL, COMPLETE, 4
C03 | Mini power center 15 kVA 480-120/240 V, NEMA 3R | EA | 1 | 1 | 0 | OUTDOOR, NEMA 3R, MINI POWER CENTER 15kVA, DRY TYPE, 480-120/240V, 3PH, 4W (Primary :3 Ph,480Vac, SEC : 120/240, 1 Ph
C04 | MicroCab 1500 outdoor DC UPS 24 VDC, NEMA 3RX | EA | 1 | 1 | 0 | OUTDOOR, NEMA 3RX, MicroCab™ 1500 Outdoor DC UPS, 24V DC, UNISTRUT MOUNTED
C05 | EMS / PPC panel (Terabase controller, gateways, switches, firewall, GPS clock) | EA | 1 | 1 | 0 | OUTDOOR, NEMA 3R , EMS PANEL, UNISTRUT MOUNTED.
C06 | Telecom panel (WAN primary + secondary) | EA | 1 | 1 | 0 | OUTDOOR, NEMA 3R , TELECOMMUNICATION PANEL, UNISTRUT MOUNTED.
D01 | 1/C 750 kcmil Cu, 15 kV, 100% EPR, MV-105 | FT | 414 | 396 | 18 | 15kV XLPE CABLE - SINGLE CORE 750MCM Copper. Cable -MV-105 EPR (3-1/C 750 MCM Cu. MV-105 EPR 100% +1/3 AL N)
D02 | 1/C #2/0 AWG Cu ground / neutral | FT | 138 | 132 | 6 | 15kV XLPE CABLE - SINGLE CORE 2/0AWG Cu (Ground Neutral) : 1-1/C #2/0 AWG Cu GND
E01 | 1/C 500 kcmil DLO tinned Cu, 2000 V, RHH/RHW-2 | FT | 2795.1 | 3240 | -444.9 | DLO CABLE, UL RHH/RHW-2 ,2000V, DC SINGLE CORE, 500kCMIL Tin coated copper phase CABLE [Supply 2000 V DC single-core 500
F01 | 1/C 250 kcmil Cu XHHW-2, 600 V | FT | 456.1 | 360 | 96.1 | CABLE, POWER, 600V, 1C, 250 MCM, COPPER, X.L.P. XHHW-2
F03 | 1/C #2 AWG Cu ground XHHW-2 | FT | 152 | 120 | 32 | CABLE, POWER, 600V, 1C #2 AWG Copper Ground, XHHW-2- For Grounding
F04 | 1/C #10 AWG Cu XHHW-2, 600 V | FT | 54.6 | 20 | 34.6 | CABLE, POWER, 600V, 1C 1/C #10 AWG Cu, XHHW-2, 600 V rated cable
F05 | 1/C #10 AWG Cu ground XHHW-2 | FT | 18.2 | 10 | 8.2 | CABLE, POWER, 600V, 1C #10 AWG Copper Ground, XHHW-2- For Grounding
F06 | 1/C #4 AWG Cu XHHW-2, 600 V | FT | 1392 | 860 | 532 | CABLE, POWER, 600V, 1C 1/C #4 AWG Cu, XHHW-2, 600 V rated cable
F07 | 1/C #8 AWG Cu ground XHHW-2 | FT | 464 | 290 | 174 | CABLE, POWER, 600V, 1C #8 AWG Copper Ground, XHHW-2- For Grounding
G01 | Cat 5e shielded | FT | 470.1 | 750 | -279.9 | #Cat 5Fe
G02 | 6-strand 50 um OM2 multimode fiber | FT | 440.1 | 100 | 340.1 | 50 µm 6 FIBER MULTIMODE OM2
J01 | Unistrut equipment rack (MB, DP, MPC, UPS, EMS, telecom) | EA | 1 | 1 | 0 | UNISTRUT STRUCTUTE TO MOUNTING MB, DP, MPC, UPA, EMS AND TELE.COMMUNICATION PANELS.
K01 | Light pole with 2 x 400 W LED floodlights | EA | 1 | 2 | -1 | FLOODLIGHT, OUTDOOR, LED, 120-208V AC,400 W LED FITTINGS.

## QA
Severity | Check | Finding | Refs
WARN | MVT_KVA | Transformer total 8400 kVA < 8421 kVA needed for 8.0 MW at 0.95 PF (before losses). Confirm AEP reactive requirement and Sineng 4.2 MVA rating basis (@50 degC).
WARN | GEOTECH_BASIS | BES-CNT01: 94.8 kip exceeds the 75 kip container load assumed in the geotech report (A254039 §2.2.1). Ask UES to confirm. | BES-CNT01
WARN | GEOTECH_BASIS | BES-CNT02: 94.8 kip exceeds the 75 kip container load assumed in the geotech report (A254039 §2.2.1). Ask UES to confirm. | BES-CNT02
WARN | GEOTECH_BASIS | BES-CNT03: 94.8 kip exceeds the 75 kip container load assumed in the geotech report (A254039 §2.2.1). Ask UES to confirm. | BES-CNT03
WARN | GEOTECH_BASIS | BES-CNT04: 94.8 kip exceeds the 75 kip container load assumed in the geotech report (A254039 §2.2.1). Ask UES to confirm. | BES-CNT04
WARN | BOM_MISMATCH | PCS-SKD01 is Sineng EH-4200-HB-UD-US-12.47 but 60% BOM B01 says: Dynapower CPS-2500 Gen5 bidirectional PCS rated 2304 kW, 690 VAC, 60 H | PCS-SKD01
WARN | BOM_MISMATCH | PCS-SKD02 is Sineng EH-4200-HB-UD-US-12.47 but 60% BOM B01 says: Dynapower CPS-2500 Gen5 bidirectional PCS rated 2304 kW, 690 VAC, 60 H | PCS-SKD02
WARN | MTO_DELTA | F01 1/C 250 kcmil Cu XHHW-2, 600 V: model 456 ft vs 60% BOM 360 ft (+27%) | F01
WARN | MTO_DELTA | F03 1/C #2 AWG Cu ground XHHW-2: model 152 ft vs 60% BOM 120 ft (+27%) | F03
WARN | MTO_DELTA | F04 1/C #10 AWG Cu XHHW-2, 600 V: model 55 ft vs 60% BOM 20 ft (+173%) | F04
WARN | MTO_DELTA | F05 1/C #10 AWG Cu ground XHHW-2: model 18 ft vs 60% BOM 10 ft (+82%) | F05
WARN | MTO_DELTA | F06 1/C #4 AWG Cu XHHW-2, 600 V: model 1392 ft vs 60% BOM 860 ft (+62%) | F06
WARN | MTO_DELTA | F07 1/C #8 AWG Cu ground XHHW-2: model 464 ft vs 60% BOM 290 ft (+60%) | F07
WARN | MTO_DELTA | G01 Cat 5e shielded: model 470 ft vs 60% BOM 750 ft (-37%) | G01
WARN | MTO_DELTA | G02 6-strand 50 um OM2 multimode fiber: model 440 ft vs 60% BOM 100 ft (+340%) | G02
INFO | ENERGY | DC nameplate 20.06 MWh vs contracted 16.0 MWh at POI
INFO | DC_ALLOC | PCS-SKD02: 2 containers (BES-CNT01, BES-CNT02), 5015 kW DC vs 5000 kW PCS | PCS-SKD02
INFO | DC_ALLOC | PCS-SKD01: 2 containers (BES-CNT03, BES-CNT04), 5015 kW DC vs 5000 kW PCS | PCS-SKD01
INFO | BEARING | STR-FDN-B1: 659 psf gross (94.8 kip equipment + 49.1 kip slab) = 33% of 2000 psf allowable | STR-FDN-B1
INFO | BEARING | STR-FDN-B2: 659 psf gross (94.8 kip equipment + 49.1 kip slab) = 33% of 2000 psf allowable | STR-FDN-B2
INFO | BEARING | STR-FDN-B3: 659 psf gross (94.8 kip equipment + 49.1 kip slab) = 33% of 2000 psf allowable | STR-FDN-B3
INFO | BEARING | STR-FDN-B4: 659 psf gross (94.8 kip equipment + 49.1 kip slab) = 33% of 2000 psf allowable | STR-FDN-B4
INFO | BEARING | STR-FDN-P1: 419 psf gross (44.1 kip equipment + 51.2 kip slab) = 21% of 2000 psf allowable | STR-FDN-P1
INFO | BEARING | STR-FDN-P2: 419 psf gross (44.1 kip equipment + 51.2 kip slab) = 21% of 2000 psf allowable | STR-FDN-P2
INFO | BEARING | STR-FDN-R1: 168 psf gross (0.7 kip equipment + 5.5 kip slab) = 8% of 2000 psf allowable | STR-FDN-R1
INFO | APPROX_LOCATION | 9 assets placed approximately (not from a dimensioned drawing) | UI-AEP-P1, UI-AEP-P2, UI-AEP-P3, UI-AEP-P4, UI-AEP-P5, UI-AXT01, UI-POL01, UI-POL02, SSV-LTG01
INFO | PROPOSED_CABLES | 8 connections are proposed and not yet in the E-403 schedule | C01, C02, C03, C04, C05, C06, C07, C08
INFO | MTO_DELTA | D01 1/C 750 kcmil Cu, 15 kV, 100% EPR, MV-105: model 414 ft vs 60% BOM 396 ft (+5%) | D01
INFO | MTO_DELTA | D02 1/C #2/0 AWG Cu ground / neutral: model 138 ft vs 60% BOM 132 ft (+5%) | D02
INFO | MTO_DELTA | E01 1/C 500 kcmil DLO tinned Cu, 2000 V, RHH/RHW-2: model 2795 ft vs 60% BOM 3240 ft (-14%) | E01